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2025		ANNUAL DRINKING WATER QUALITY REPORT
PWSID #:  1150004		NAME:  Avon Wheel MHP	

Este informe contiene información importante acerca de su agua potable.  Haga que alguien lo traduzca para usted, ó hable con alguien que lo entienda.  (This report contains important information about your drinking water.  Have someone translate it for you, or speak with someone who understands it.)

WATER SYSTEM INFORMATION:
[bookmark: Text33]This report shows our water quality and what it means.  If you have any questions about this report or concerning your water utility, please contact Thomas Heist		at
[bookmark: Text34]717-587-4172		.  We want you to be informed about your water supply.  

SOURCE(S) OF WATER:
Our water source

	The facility is supplied by two wells located on the property.



A Source Water Assessment of our sources was completed by the PA Department of Environmental Protection (Pa. DEP).  The Assessment has found that our source(s) of is/are potentially most susceptible to [insert potential Sources of Contamination listed in your Source Water Assessment Summary].  Overall, our source have moderate risk of significant contamination.  A summary report of the Assessment is available on the Source Water Assessment Summary Reports eLibrary web page:  Source Water Assessment Folder.  Complete reports were distributed to municipalities, water supplier, local planning agencies and PADEP offices.  Copies of the complete report are available for review at the Pa. DEP.
Regional Office, Records Management Unit at (717) 705-4732.

Some people may be more vulnerable to contaminants in drinking water than the general population.  Immuno‑compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections.  These people should seek advice about drinking water from their health care providers.  EPA/CDC guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline (800‑426‑4791).

[bookmark: _Toc223421969]Monitoring Your Water:
We routinely monitor for contaminants in your drinking water according to federal and state laws.  The following tables show the results of our monitoring for the period of January 1 to December 31, 2025.  The State allows us to monitor for some contaminants less than once per year because the concentrations of these contaminants do not change frequently.  Some of our data is from prior years in accordance with the Safe Drinking Water Act.  The date has been noted on the sampling results table.

DEFINITIONS:
Action Level (AL) – The concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow.
Maximum Contaminant Level (MCL) – The highest level of a contaminant that is allowed in drinking water.  MCLs are set as close to the MCLGs as feasible using the best available treatment technology.
Maximum Contaminant Level Goal (MCLG) – The level of a contaminant in drinking water below which there is no known or expected risk to health.  MCLGs allow for a margin of safety.
Maximum Residual Disinfectant Level (MRDL) – The highest level of a disinfectant allowed in drinking water.  There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.
Maximum Residual Disinfectant Level Goal (MRDLG) – The level of a drinking water disinfectant below which there is no known or expected risk to health.  MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.
Minimum Residual Disinfectant Level (MinRDL) – The minimum level of residual disinfectant required at the entry point to the distribution system.
Level 1 Assessment – A Level 1 assessment is a study of the water system to identify potential problems and determine (if possible) why total coliform bacteria have been found in our water system.
[bookmark: _Hlk181365718]Level 2 Assessment – A Level 2 assessment is a very detailed study of the water system to identify potential problems and determine (if possible) why an E. coli MCL violation has occurred and/or why total coliform bacteria have been found in our water system on multiple occasions.
Treatment Technique (TT) – A required process intended to reduce the level of a contaminant in drinking water.

Mrem/year = millirems per year (a measure of radiation absorbed by the body)
pCi/L = picocuries per liter (a measure of radioactivity)
ppb = parts per billion, or micrograms per liter (μg/L)
ppm = parts per million, or milligrams per liter (mg/L)
ppq = parts per quadrillion, or picograms per liter
ppt = parts per trillion, or nanograms per liter
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DETECTED SAMPLE RESULTS:
	Chemical Contaminants

	Contaminant
	MCL in CCR Units
	MCLG
	Level Detected
	Range of Detections
	Units
	Sample Date
	Violation Y/N
	Sources of Contamination

	Chlorine
	4
	4
	1.32
	1.32-1.63
	ppm
	Mar 2025
	N
	Water additive used to control microbes

	Nitrate
	10
	10
	5.38
	4.84-5.73
	ppm
	10/2/2025
	N
	Runoff from fertilizer

	Arsenic
	10
	10
	5
	n/a
	ppb
	2021
	N
	Erosion of natural deposits

	HAA5
	60
	n/a
	1.12
	1-1.12
	ppb
	2021
	N
	By-product of drinking water disinfection

	TTHM
	80
	n/a
	5.6
	0.7-5.6
	ppb
	2024
	N
	By-product of drinking water disinfection

	Combine Uranium
	20
	n/a
	3.685
	n/a
	pCi/L
	2022
	N
	Naturally occurring in soil

	Fluoride
	2
	n/a
	0.1
	n/a
	ppm
	2024
	N
	Erosion of natural deposits;Water additive which promotes strong teeth. Discharge from fertilizer and aluminum factories

	Gross Alpha
	15
	n/a
	5.07
	n/a
	pCi/L
	2025
	N
	Naturally occurring in soil

	Perfluorooctanesulfonic Acid (PFOS)
	18
	n/a
	9.057
	8-11.43
	ppt
	2025
	N
	Discharge from Mfg.facilities and run-off from land use activities.

	Perfluorooctanic Acid (PFOA)
	14
	n/a
	7.33
	6.3-9.32
	ppt
	2025
	N
	Discharge from Mfg. facilities and run-off from land use activities.


[bookmark: _Toc223421970]*EPA’s MCL for fluoride is four ppm.  However, Pennsylvania has set a lower MCL to better protect human health.

	Entry Point Disinfectant Residual

	Contaminant
	Minimum Disinfectant
Residual
	Lowest
Level Detected
	Range of Detections
	Units
	Sample Date
	Violation Y/N
	Sources of Contamination

	Chlorine
	0.40
	0.41
	0.41-222
	ppm
	10/30/25
	N
	Water additive used to control microbes.












	Lead and Copper

	Contaminant
	Action Level (AL)
	MCLG
	90th Percentile Value
	Range of tap sampling results
	Units
	# of Sites Above AL of Total Sites
	Violation Y/N
	Sources of
Contamination

	Lead
	15
	0
	0
	0
	ppb
	0 of 5
	N
	Corrosion of household plumbing.

	Copper
	1.3
	1.3
	0
	0
	ppm
	0 of 5
	N
	Corrosion of household plumbing.






[bookmark: _Toc223421971]DETECTED CONTAMINANTS HEALTH EFFECTS LANGUAGE AND CORRECTIVE ACTIONS:
	Infants below the age of six months who drink water containing nitrate in excess of the MCL could become seriously ill and, if untreated, may die. Symptoms includes shortness of breath and blue baby syndrome.



OTHER VIOLATIONS:
	No Violations



EDUCATIONAL INFORMATION:
The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs and wells.  As water travels over the surface of the land or through the ground, it dissolves naturally‑occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.  Contaminants that may be present in source water include:
Microbial contaminants, such as viruses and bacteria, which may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife.
· Inorganic contaminants, such as salts and metals, which can be naturally‑occurring or result from urban stormwater run‑off, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.
· Pesticides and herbicides, which may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses.
· Organic chemical contaminants, including synthetic and volatile organic chemicals, which are by‑products of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, and septic systems.
· Radioactive contaminants, which can be naturally‑occurring or be the result of oil and gas production and mining activities.
In order to ensure that tap water is safe to drink, EPA and DEP prescribes regulations which limit the amount of certain contaminants in water provided by public water systems.  FDA and DEP regulations establish limits for contaminants in bottled water which must provide the same protection for public health.
Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that water poses a health risk.  More information about contaminants and potential health effects can be obtained by calling the Environmental Protection Agency’s Safe Drinking Water Hotline (800‑426‑4791).
Information about Lead
Lead can cause serious health problems, especially for pregnant women and young children.  Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. Avon Wheel MHP is responsible for providing high quality drinking water and is removing lead pipes, but cannot control the variety of materials used in plumbing components in your home.  You share the responsibility for protecting yourself and your family from the lead in your home plumbing.  You can take responsibility by identifying and removing lead materials within your home plumbing and taking steps to reduce your family’s risk.  Before drinking tap water, flush your pipes for several minutes by running your tap, taking a shower, doing laundry or a load of dishes.  You can also use a filter certified by an American National Standards Institute accredited certifier to reduce lead in drinking water.  If you are concerned about lead in your water and wish to have your water tested, contact Avon Wheel office.  Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available at http://www.epa.gov/safewater/lead.

OTHER INFORMATION:
	Nitrate: Nitrate in drinking water at levels above 10 ppm is a health risk for infants of less than six months of age. High nitrate levels in drinking water can cause blue baby syndrome. Nitrate levels may rise quickly for short periods of time because of rainfall or agricultural activity. If you are caring for an infant, you should ask for advice from your health care provider.



Avon Wheel MHP prepared a service line inventory that includes the type of materials contained in each service line in our distribution system.  This inventory can be accessed by contacting the office.
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